PROJECT ENGINEER RESPONSIBILITY:  This is a general specification guide, intended to be used by experienced construction professionals, in conjunction with good construction practice and professional judgment.  This guide is to aid in the creation of a complete building specification that is to be fully reviewed and edited by the engineer.  Sections of this guide should be included, edited, or omitted based on the requirements of a specific project.  It is the responsibility of both the specifier and the purchaser to determine if a product or system is suitable for its intended use.  Neither Owens Corning, nor any of its subsidiary or affiliated companies, assume any responsibility for the content of this specification guide relative to actual projects and specifically disclaim any and all liability for any errors or omissions in design, detail, structural capability, attachment details, shop drawings or other construction related details, whether based upon the information provided by Owens Corning or otherwise.

SECTION 23 07 13

DUCT INSULATION

Note to Specifier: This specification is offered as a guide to specifiers and should be employed at the discretion of the user.  The ultimate design and installation are the responsibility of the Engineer or Architect.

GENERAL

SUMMARY

Section Includes:  Provide fibrous glass duct liner in spiral (round) sheet metal ducts for commercial air duct systems.

Note to Specifier: The following temperature ranges are typical for these systems. However, if project requirements call for service temperatures outside the above ranges, consult the manufacturer's published data to determine operating temperature limitations of the insulation product or products under consideration.

Air duct systems operating at internal air velocities not exceeding rated duct liner limitations as listed below, and internal air temperatures not exceeding 250°F (121°C).

REFERENCES

Duct liner insulation materials shall meet the requirements of one or more of the following specifications as applicable to the specific product or end use:

American Society for Testing of Materials (ASTM):

ASTM C1071, Standard Specification for Thermal and Acoustical Insulation (Glass Fiber, Duct Lining Material).

ASTM C916, Standard Specification for Adhesives for Duct Thermal Insulation.

ASTM C1338, Test Method for Determining Fungi resistance of Insulation Materials and Facings

ASTM E84, Standard Test Method for Surface Burning Characteristics of Building Materials.

Underwriters Laboratories (UL)

UL 723, Test for Surface Burning Characteristics of Building Materials.

National Fire Protection Association (NFPA):

NFPA 90A, Standard for the Installation of Air-Conditioning and Ventilating Systems.

NFPA 90B, Standard for the Installation of Warm Air Heating and Air-Conditioning Systems.

SUBMITTALS

Product Data: Submit product characteristics, performance criteria, and limitations, including installation instructions, for each type of product indicated.

For adhesives and sealants, submit documentation including printed statement of VOC content.

Sustainable Design Submittals:  Submit manufacturer’s sustainable design certifications as specified.

Qualification Data:  For Installer.

QUALITY ASSURANCE

Installer Qualifications:  A qualified installer who has been trained by and is acceptable to manufacturer to install manufacturer's products.

Delivery and Storage of Materials

Delivery:  Deliver materials in manufacturer’s original packaging.

Storage:  Store and protect products in accordance with manufacturer’s instructions. Store in a dry indoors location.  Protect insulation materials from moisture and soiling.

Do not install insulation that has been damaged or wet.  Remove it from jobsite.

PRODUCTS

MANUFACTURER

Owens Corning Insulating Systems, LLC, Toledo, OH  43659; www.owenscorning.com.

Duct INSULATION

General:

Spiral Duct Liner:  Rigid, resin bonded fibrous glass board with a damage-resistant, flame retardant veil faced airstream surface with a reinforced aluminum foil (FRK) backing.

Owens Corning QuietZone® Spiral Duct Liner insulation is not known to contain penta-, octa, or deca-brominated diphenyl flame retardant substances, such as deca-Bromine (deca-BDE).

Certifications:

QuietZone® Spiral Duct Liner is GREENGUARD Indoor Air Quality Certified® and GREENGUARD Children & Schools Certified℠.

QuietZone® Spiral Duct Liner is GREENGUARD Children & Schools Certified℠ for dimensions up to and including 1” thickness.

QuietZone® Spiral Duct Liner is certified by Scientific Certification Systems (SCS) to contain a minimum of 57% recycled glass content.

Spiral duct liner product is UL listed and labeled.

Duct Insulation: For service at internal air velocities not to exceed 6,000 fpm (30.5 m/s), provide the following:

Acceptable Product:  Owens CorningTM QuietZone® Spiral Duct Liner.

Sizes: 1 in and 1-1/2 in (25mm and 38mm) thickness.

Fabricated with a glass mat on the airstream side, to resist damage during installation and in service.

ACCESSORY MATERIALS

Accessories:  Provide accessories per duct insulation system manufacturer’s recommendations, including the following:

Adhesives For Indoor Applications:  VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

EXECUTION

EXAMINAtion

Verify that materials and accessories can be installed in accordance with Contract Documents and material manufacturers' recommendations.

Verify, by inspecting product labeling, submittal data, and/or certifications which may accompany the shipments, that materials and accessories to be installed on the project comply with applicable specifications and standards and meet specified thermal and physical properties.

Before starting work under this section, carefully inspect the site and installed work of other trades and verify that such work is complete to the point where installation of materials and accessories under this section can begin.

Safety Precautions

Insulation contractor's employees shall be properly protected during installation of insulation.  Protection shall include proper attire when handling and applying insulation materials, and shall include, but not be limited to, disposable dust respirators, gloves, hard hats, and eye protection.

INSTALLATION

Installation needs to be performed by an Owens Corning trained installer. Completely cover duct designated to receive duct liner.  Neatly butt transverse joints without interruptions or gaps. Install the mat faced surface of the duct liner facing the airstream.

Complying with requirements of ASTM C916, adhere duct liner to the sheet metal with 90% coverage of adhesive.

Coat exposed leading edges and transverse joints during fabrication.

Do not coat the grooved longitudinal edges.

Do not install two layers of duct liner to meet a specified liner thickness.

FIELD QUALITY ASSURANCE

Upon completion of insulation work and before operation is to commence, visually inspect the work and verify that it has been correctly installed.

Open all system dampers and turn on fans to blow all scraps and other loose pieces of material out of the duct system. Allow for a means of removal of such material.

Check the duct system to ensure that there are no air leaks through joints.

PROTECTION

Replace damaged insulation, which cannot be satisfactorily repaired, including insulation with duct liner damage and moisture-saturated insulation.

The insulation contractor shall advise the general and/or the mechanical contractor as to requirements for protection of the insulation work during the remainder of the construction period, to avoid damage and deterioration of the finished insulation work.

END OF SECTION

©2013 Owens Corning. All Rights Reserved.